## Introduction
Double click to access
BioWATT (Biogas Wastewater Assessment Technology Tool) | v1.0 (19 Jan 2016)
Below are basic instructions for using the Biogas Wastewater Assessment Technology Tool (BioWATT). More detailed information about BioWATT and the wastewater-to-energy technologies evaluated by the tool is contained in the BioWATT User Guide (embedded as a pdf at the top of each worksheet). Most users should enter data and view results in the “Basic Module” worksheet. This worksheet uses standard defaults to produce results. Users with more advanced knowledge of wastewater treatment can use the “Advanced Module” worksheet to enter more specific data and/or overwrite defaults included in the tool to develop more refined results. 1. Enter project specific data into the GREEN cells. - On the “Basic Module” worksheet, inputs are in the “INPUT DATA” section. - On the “Advanced Module” worksheet, more detailed inputs are available across the various wastewater-to-energy technologies evaluated by the tool. 2. View Results - Summary results for the wastewater-to-energy technologies evaluated are shown in the “Basic Module” worksheet under “SUMMARY OUTPUT RESULTS.” (All output results are calculated in the “Advanced Module” worksheet. Selected values in the “Advanced Module” worksheet are copied into the “SUMMARY OUTPUT RESULTS” section of the “Basic Module” worksheet.) All Outputs in both the "Basic Module" and "Advanced Module" worksheets are in ORANGE cells. - More detailed results and data related to the wastewater-to-energy technologies evaluated by BioWATT can be seen in the “Advanced Module” worksheet. This is true whether the user relies on the tool’s standard defaults or if the user chooses to enter more specific data and/or overwrite defaults in the “Advanced Module” worksheet. In both the "Basic Module" and "Advanced Module" worksheets, explanatory comments and/or field instructions are included for selected inputs and outputs.

## Basic Module
BioWATT (Biogas Wastewater Assessment Technology Tool) |  |  | v1.0 (19 Jan 2016)
Project: | (Name of WWTP) |  |  | Double click to access
Date: | (Date)
INPUT DATA
WASTEWATER ENTERING WWTP | Value | Unit | Comment
Average hydraulic load | 40000 | m3/d | Provide estimate of the expected average daily wastewater flow reaching the WWTP. A rough estimate can be made by utilizing about 80% of the water supply to the same catchment, and by adding an assumption for stormwater flow and ground-water intrusion. For separate sewer systems this may add up to another 30% flow, for combined sewer systems this may add up to another 100-200%. |  | 1000
Average inflow BOD5 concentration | 120 | mg/L | Provide estimate of the expected average BOD5 concentration entering the WWTP. |  | 565
GREENHOUSE GAS EMISSIONS | Value | Unit | Comment |  | 100
Local GHG emissions for electricity generation | 565 | g CO2/kWh | Select appropriate value from drop-down menu, or utilize data from other sources (e.g. International Energy Agency IEA: "CO2 Emissions From Fuel Combustion")
Do you have a UASB that is not collecting biogas? | NO |  | Select "YES" or "NO" from drop-down menu |  | YES
Do you have an Anaerobic Pond that is not collecting biogas? | NO |  | Select "YES" or "NO" from drop-down menu |  | NO
UNIT COST | Value | Unit | Comment
Electricity tariff | 0.15 | US$/kWh | Insert locally prevailing unit cost for power purchase from public grid
Sludge disposal unit cost | 10 | US$/m3 | Insert locally prevailing unit cost for sludge disposal / reuse
Average labor cost | 10000 | US$/personnel/year | Insert locally prevailing average unit cost for operators at WWTP
SUMMARY OUTPUT RESULTS
CAS + DIGESTER | Result | Unit | Comment
Biogas production | 567648 | m³/year
Electricity generation from biogas | 1106913.6 | kWh/year
Including co-digestion | NO | ---
Including ultrasound sludge disintegration | NO | ---
GHG emission reduction through electricity from biogas | -625.4062 | tons CO2e/year
Elimination of existing GHG emissions from digester | 0 | tons CO2e/year
Total GHG emission reduction | -625.4062 | tons CO2e/year
Reduction of electricity cost | -166037.04 | US$/year
Reduction of aeration cost in aeration tank | -75600 | US$/year
Reduction of sludge disposal cost | -28336.6957 | US$/year
Additional O&M cost | 52353.3823 | US$/year
Total OPEX saving | -217620.3534 | US$/year
Digester | 1658.5714 | m³
Biogas holder | 311.04 | m³
CHP - total electric power | 151.632 | kW
TRICKLING FILTER + DIGESTER | Result | Unit | Comment
Biogas production | 541893.6 | m³/year
Electricity generation from biogas | 1056692.52 | kWh/year
Including co-digestion | NO | ---
GHG emission reduction through electricity from biogas | -597.0313 | tons CO2e/year
Elimination of existing GHG emissions from digester | 0 | tons CO2e/year
Total GHG emission reduction | -597.0313 | tons CO2e/year
Reduction of electricity cost | -158503.878 | US$/year
Reduction of sludge disposal cost | -26843.687 | US$/year
Additional O&M cost | 52353.3823 | US$/year
Total OPEX saving | -132994.1827 | US$/year
Digester | 1574.5714 | m³
Biogas holder | 296.928 | m³
CHP - total electric power | 144.7524 | kW
UASB | Result | Unit | Comment
Biogas production | 380184 | m³/year
Electricity generation from biogas | 741358.8 | kWh/year
GHG emission reduction through electricity from biogas | -418.8677 | tons CO2e/year
Elimination of existing GHG emissions from UASB | 0 | tons CO2e/year
Total GHG emission reduction | -418.8677 | tons CO2e/year
Reduction of electricity cost | -111203.82 | US$/year
Additional O&M cost | 17413.2287 | US$/year
Total OPEX saving | -93790.5913 | US$/year
Biogas holder | 208.32 | m³
CHP - total electric power | 101.556 | kW
COVERED ANAEROBIC POND | Result | Unit | Comment
Biogas production | 450514.2857 | m³/year
Electricity generation from biogas | 946080 | kWh/year
GHG emission reduction through electricity from biogas | -534.5352 | tons CO2e/year
Elimination of existing GHG emissions from Ana.Ponds | 0 | tons CO2e/year
Total GHG emission reduction | -534.5352 | tons CO2e/year
Reduction of electricity cost | -141912 | US$/year
Additional O&M cost | 24848.8362 | US$/year
Total OPEX saving | -117063.1638 | US$/year
CHP - total electric power | 129.6 | kW
De-locking key: W2E

## Advanced Module
BioWATT (Biogas Wastewater Assessment Technology Tool) |  |  | v1.0 (19 Jan 2016)
Project: | (Name of WWTP) |  |  | Double click to access
Date: | (Date)
GENERAL DATA | Value | Unit | Comment
WASTEWATER ENTERING WWTP
Average hydraulic load | 40000 | m³/d
Average inflow BOD5 concentration | 120 | mg/L
Average TSS/ BOD5 concentration | 1 | --- | Typical: 1.00 (0.8-1.2)
Average inflow TSS concentration | 120 | mg/L | Typical: same value as for BOD5 concentration
Average VSS/TSS concentration | 0.75 | --- | Typical: VSS/TSS = 0.75 (0.6-0.85); in case of dominant number of septic tanks in the catchment it may go down to 0.2-0.3
Average inflow VSS concentration | 90 | mg/L
Local capita-specific BOD5 production | 50 | gBOD5/cap/d | Select appropriate value from drop-down menu, or utilize data from other sources |  | 60
Average pollution load (BOD5) | 4800 | kg/d |  |  | 50
Average pollution load in population equivalents(60) | 80000 | PE60 | (Note: 1 PE60 = 60 g BOD5/d) |  | 40
Average pollution load in population equivalents (local) | 96000 | cap | (Note: 1 cap = xx g BOD5/d, according to project specific input data)
CAS + SLUDGE DIGESTER | Value | Unit | Comment
WASTEWATER TREATMENT
▪ Primary Sedimentation Tank (PST)
PST foreseen? | YES |  | Select "YES" or "NO" from drop-down menu "YES" (recommended when influent TSS > 80 mg/L), "NO" (recommended when influent TSS < 80 mg/L) |  | YES
Volume PST | 1250 | m³ |  |  | NO
Average retention time in PST | 0.75 | h | Typical: 0.75 (0.50-1.5) at average hydraulic load
BOD5 removal efficiency of PST | 30 | % | Typical: 30 (20-35)
TSS removal efficiency of PST | 50 | % | Typical: 50 (50-65)
▪ Aeration Tank (AT)
Average influent BOD5 load | 3360 | kg/d
Average influent TSS load | 2400 | kg/d
SLUDE PRODUCTION
▪ Primary sludge
Daily PS production (DS) | 2400 | kgDS/d
DS of primary sludge after thickening | 3.5 | %DS | Gravity thickener: 2-6%. Mechanical thickener: 5-7%.
VS/DS of primary sludge after thickening | 75 | %VS | Typical: VSS/TSS = 0.75 (0.6-0.85); in case of many septic tanks it may go down to 0.2-0.3
Daily PS production, thickened sludge (m3) | 68.5714 | m³/d
▪ Secondary sludge
Daily raw WAS production (DS) | 0.75 | gDS/gBOD5 | Typical: 0.75 (0.5-1.2), dependent on influent TSS, sludge age, temperature.
| 2520 | kgDS/d
DS of WAS after thickening | 6 | %DS | Gravity thickener: 2-4%. Mechanical thickener: 5-7%.
VS/DS of WAS after thickening | 70 | %VS | (i) sludge age ≈ 5-10 days: avg. 70% (65-75%), (ii) sludge age ≈ 10-15 days: avg. 68% (62-75%), (iii) sludge age > 20 days: avg. 65% (60-70%)
Daily WAS production, thickened sludge (m3) | 42 | m³/d
CO-DIGESTION OF ORGANIC WASTE
Sludge treatment shall include co-digestion? | NO |  | Select "YES" or "NO" from drop-down menu |  | YES
Type of organic feedstock |  |  | Describe type of organic feedstock |  | NO
Average daily quantity of feedstock | 0 | m³/d
DS of organic feedstock | 5 | % of weight | Select appropriate value from drop-down menu, or utilize data from other sources |  | 5 | 90
VS/DS of organic feedstock | 90 | %VS | Select appropriate value from drop-down menu, or utilize data from other sources |  | 10 | 90
SLUDGE DISINTEGRATION with ULTRASOUND |  |  |  |  | 5 | 95
Sludge treatment shall include sludge ultrasound treatment prior to digester? | NO | --- | Select "YES" or "NO" from drop-down menu
Expected increase of biogas yield from sludge | 0 | % | Typical: +20% (10-30%)
DIGESTER
Digester retention time | 15 | days | (i) mesophilic digester (30-38°C): >15 d (large WWTPs), >20 d (medium, small WWTPs). (ii) ambient temperature: see figure
Required digester volume | 1658.5714 | m³
▪ m3/d feeding
Average feeding of PS | 68.5714 | m³/d
Average feeding of WAS | 42 | m³/d
Average feeding of organic feedstock | 0 | m³/d
Total average feeding | 110.5714 | m³/d
▪ DS feeding
Average feeding of PS | 2400 | kgDS/d
Average feeding of WAS | 2520 | kgDS/d
Average feeding of organic feedstock | 0 | kgDS/d
Total average feeding | 4920 | kgDS/d
▪ VS feeding
Average feeding of PS | 1800 | kgVS/d
Average feeding of WAS | 1764 | kgVS/d
Average feeding of organic feedstock | 0 | kgVS/d
Total average feeding | 3564 | kgVS/d
▪ VS destruction (%)
Average VS destruction of PS | 60 | % of VS | Typical: 55-60%
Average VS destruction of WAS | 40 | % of VS | Typical: 30-40%
Average VS destruction of organic feedstock | 85 | % of VS | Select appropriate value from drop-down menu, or utilize data from other sources |  | 85
▪ VS destruction (kgVS) |  |  |  |  | 80
Average VS destruction of PS | 1080 | kgVSdestroyed/d |  |  | 95
Average VS destruction of WAS | 705.6 | kgVSdestroyed/d
Average VS destruction of organic feedstock | 0 | kgVSdestroyed/d
Total average VS destruction | 1785.6 | kgVSdestroyed/d
SLUDGE FOR DISPOSAL / REUSE
DS after sludge dewatering | 23 | %DS | Typical: 23 (18-35)
Total average DS production | 3134.4 | kgDS/d
Total specific DS production | 39.18 | gDS/PE60/d
| 32.65 | gDS/cap/d
Total average dewatered sludge production | 13.6278 | m³/d
| 4974.1565 | m³/year
BIO GAS PRODUCTION
Biogas holder volume | 20 | % of daily gas production | Typical: 20 (10-30)% for large-small WWTPs
Required biogas holder volume | 311.04 | m³
▪ Biogas yield
Biogas yield from PS | 950 | L/kgVSdestroyed | Typical: 950 (900-1000)
Biogas yield from WAS | 750 | L/kgVSdestroyed | Typical: 750 (700-800)
Biogas yield from organic feedstock | 1000 | L/kgVSdestroyed | Select appropriate value from drop-down menu, or utilize data from other sources |  | 1100
▪ Biogas production |  |  |  |  | 1000
Biogas production from PS | 1026 | m³/d |  |  | 850
Biogas production from WAS | 529.2 | m³/d
Biogas production from organic feedstock | 0 | m³/d
Biogas production from ultrasound treatment | 0 | m³/d
Total biogas production | 1555.2 | m³/d
| 567648 | m³/year
Total specific biogas production | 19.44 | L/PE60/d
| 16.2 | L/cap/d
▪ Methane content of biogas
Methane in biogas from PS+WAS | 65 | % CH4 | Typical: 65 (60-70%)
Methane in biogas from organic feedstock | 60 | % CH4 | Select appropriate value from drop-down menu, or utilize data from other sources
Methane in total biogas production | 65 | % CH4
ENERGY FROM BIOGAS
Calorific value of biogas | 6.5 | kWh/m3
▪ Electricity generation
CHP: Electric energy generation efficiency | 30 | % | Typical: co-generation: 30-40%, microturbine: 28-33%, or see figure
Electricity generation from biogas | 3032.64 | kWh/d |  |  | 75
| 13.8364 | kWh/PE60/year |  |  | 60
| 1106913.6 | kWh/year |  |  | 53
Electricity consumption of CAS-WWTP | 35 | kWh/PE60/year | Typical: 20-50 or see table
| 7671.2329 | kWh/d
| 2800000 | kWh/year
Electricity coverage of WWTP from biogas | 39.53% | % of consumption
▪ Thermal energy generation
CHP: Thermal energy generation efficiency | 50 | % | Typical: 50 (50-55)%
Thermal energy generation | 5054.4 | kWh/d
| 1844856 | kWh/year
GREENHOUASE GAS (GHG) EMISSIONS REDUCTION
Local GHG emissions for electricity generation | 565 | g CO2/kWh
Production of electricity from renewable biogas | 1106913.6 | kWh/year
GHG emission reduction through electricity from biogas | -625.4062 | tons CO2e/year | This is the (saved) fossil CO2e emission that is avoided through renewable biogas utilization for power generation.
Elimination of existing GHG emissions from digester | 0 | tons CO2e/year | The biogas in question can only be considered if it was emitted already before this project; if the biogas is generated and utilized by the project, it cannot be considered an emission reduction.
Total GHG emission reduction | -625.4062 | tons CO2e/year
OPEX SAVINGS
Electricity tariff | 0.15 | US$/kWh
Reduction of electricity cost | -454.896 | US$/d | (Saving equals electricity production from biogas)
| -166037.04 | US$/year
Reduction of aeration cost in aeration tank | -1380.8219 | kWh/d | (The value, which is calculated here is based upon a comparison with Extended Aeration without PST. The following assumptions are made: (i) aeration requires 60% of total WWTP electricity consumption, (ii) introduction of PST reduces aeration requirement according to its BOD removal efficiency.)
| -504000 | kWh/year
| -75600 | US$/year
Sludge disposal unit cost | 10 | US$/m3
Reduction of sludge disposal cost | -7.7635 | m³/d
| -2833.6696 | m³/year
| -28336.6957 | US$/year
Additional labor hour cost | 10000 | US$/personnel/year
| 15000 | US$/year | (The value, which is calculated here is based upon the following assumptions: (i) a modern Western WWTP requires additional 0.5 USD/PE60/y for running the digestion system, (ii) the WWTP of this project will require 50% more personnel than the Western plant due to not-so-perfect efficiencies, (iii) TOTAL operator cost at a Western WWTP is assumed as 40,000 US$/year)
Additional maintenance cost | 37353.3823 | US$/year | (The value, which is calculated here is based upon the following assumptions: (i) Additional maintenance cost equals 1%/year of European CAPEX requirement for a mesophilic sludge digestion system, (ii) European CAPEX requirement for digestion system equals 81098 x PE60 (-0.684), (iii) EUR/US$ = 1.3)
Total OPEX saving | -217620.3534 | US$/year
INSTALLATION REQUIREMENTS
Primary Sedimentation Tank | 1250 | m³
Pre-treatment of organic waste | Check specific requirements! | ---
Ultrasound sludge disintegration installations | NO | ---
Reduction of Aeration Tank volume | -30% | %
Digester volume | 1658.5714 | m³
Biogas holder | 311.04 | m³
CHP - total electric power | 151.632 | kW | Assumption: avg. operation time = 20 h/d
| 75.816 | kW / unit | Based on 2 units
Biogas cleaning | Check specific requirements! | ---
Biogas pipe system, flare, etc | Check specific requirements! | ---
TRICKLING FILTER + SLUDGE DIGESTER | Value | Unit | Comment
WASTEWATER TREATMENT
▪ Primary Sedimentation Tank (PST)
PST foreseen? | YES |  | Select "YES" or "NO" from drop-down menu "YES" (recommended when influent TSS > 80 mg/L), "NO" (recommended when influent TSS < 80 mg/L)
Volume PST | 1250 | m³
Average retention time in PST | 0.75 | h | Typical: 0.75 (0.50-1.5) at average hydraulic load
BOD5 removal efficiency of PST | 30 | % | Typical: 30 (20-35)
TSS removal efficiency of PST | 50 | % | Typical: 50 (50-65)
▪ TRICKLING FILTER (TF)
Average influent BOD5 load | 3360 | kg/d
Average influent TSS load | 2400 | kg/d
SLUDE PRODUCTION
▪ Primary sludge
Daily PS production (DS) | 2400 | kgDS/d
DS of primary sludge after thickening | 3.5 | %DS | Gravity thickener: 2-6%. Mechanical thickener: 5-7%.
VS/DS of primary sludge after thickening | 75 | %VS | Typical: VSS/TSS = 0.75 (0.6-0.85); in case of many septic tanks it may go down to 0.2-0.3
Daily PS production, thickened sludge (m3) | 68.5714 | m³/d
▪ Secondary sludge
Daily raw TFS production (DS) | 0.65 | gDS/gBOD5 | Typical: 0.65 (0.5-1.0), dependent on influent TSS, filter loading, temperature.
| 2184 | kgDS/d
DS of TFS after thickening | 6 | %DS | Gravity thickener: 2-4%. Mechanical thickener: 5-7%.
VS/DS of TFS after thickening | 70 | %VS | Typical: 70% (65-75%)
Daily TFS production, thickened sludge (m3) | 36.4 | m³/d
CO-DIGESTION OF ORGANIC WASTE
Sludge treatment shall include co-digestion? | NO |  | (Same assumption as above for CAS + Digestion)
Type of organic feedstock | 0 |  | (Same assumption as above for CAS + Digestion)
Average daily quantity | 0 | m³/d | (Same assumption as above for CAS + Digestion)
DS of organic feedstock | 5 | % of weight | (Same assumption as above for CAS + Digestion)
VS/DS of organic feedstock | 90 | %VS | (Same assumption as above for CAS + Digestion)
DIGESTER
Digester retention time | 15 | days | (i) mesophilic digester (30-38°C): >15 d (large WWTPs), >20 d (medium, small WWTPs). (ii) ambient temperature: see figure
Required digester volume | 1574.5714 | m³
▪ m3/d feeding
Average feeding of PS | 68.5714 | m³/d
Average feeding of TFS | 36.4 | m³/d
Average feeding of organic feedstock | 0 | m³/d
Total average feeding | 104.9714 | m³/d
▪ DS feeding
Average feeding of PS | 2400 | kgDS/d
Average feeding of WAS | 2184 | kgDS/d
Average feeding of organic feedstock | 0 | kgDS/d
Total average feeding | 4584 | kgDS/d
▪ VS feeding
Average feeding of PS | 1800 | kgVS/d
Average feeding of WAS | 1528.8 | kgVS/d
Average feeding of organic feedstock | 0 | kgVS/d
Total average feeding | 3328.8 | kgVS/d
▪ VS destruction (%)
Average VS destruction of PS | 60 | % of VS | (Same assumption as above for CAS + Digestion)
Average VS destruction of TFS | 40 | % of VS | (Same assumption as above for CAS + Digestion)
Average VS destruction of organic feedstock | 85 | % of VS | (Same assumption as above for CAS + Digestion)
▪ VS destruction (kgVS)
Average VS destruction of PS | 1080 | kgVSdestroyed/d
Average VS destruction of WAS | 611.52 | kgVSdestroyed/d
Average VS destruction of organic feedstock | 0 | kgVSdestroyed/d
Total average VS destruction | 1691.52 | kgVSdestroyed/d
SLUDGE FOR DISPOSAL / REUSE
DS after sludge dewatering | 23 | %DS | (Same assumption as above for CAS + Digestion)
Total average DS production | 2892.48 | kgDS/d
Total specific DS production | 36.156 | gDS/PE60/d
| 30.13 | gDS/cap/d
Total average dewatered sludge production | 12.576 | m³/d
| 4590.24 | m³/year
BIO GAS PRODUCTION
Biogas holder volume | 20 | % of daily gas production | (Same assumption as above for CAS + Digestion)
Required biogas holder volume | 296.928 | m³
▪ Biogas yield
Biogas yield from PS | 950 | L/kgVSdestroyed | (Same assumption as above for CAS + Digestion)
Biogas yield from TFS | 750 | L/kgVSdestroyed | (Same assumption as above for CAS + Digestion)
Biogas yield from organic feedstock | 1000 | L/kgVSdestroyed | (Same assumption as above for CAS + Digestion)
▪ Biogas production
Biogas production from PS | 1026 | m³/d
Biogas production from TFS | 458.64 | m³/d
Biogas production from organic feedstock | 0 | m³/d
Total biogas production | 1484.64 | m³/d
| 541893.6 | m³/year
Total specific biogas production | 18.558 | L/PE60/d
| 15.465 | L/cap/d
▪ Methane content of biogas
Methane in biogas from PS+TFS | 65 | % CH4 | (Same assumption as above for CAS + Digestion)
Methane in biogas from organic feedstock | 60 | % CH4 | (Same assumption as above for CAS + Digestion)
Methane in total biogas production | 65 | % CH4
ENERGY FROM BIOGAS
Calorific value of biogas | 6.5 | kWh/m3
▪ Electricity
Electric energy generation efficiency | 30 |  | (Same assumption as above for CAS + Digestion)
CHP: Electricity generation from biogas | 2895.048 | kWh/d
| 13.2087 | kWh/PE60/year
| 1056692.52 | kWh/year
Electricity consumption of TF-WWTP | 15 | kWh/PE60/year | Typical: 15 (8-38), dependant on power consumption requirements for treatment stages other than Trickling Filter
| 3287.6712 | kWh/d
| 1200000 | kWh/year
Electricity coverage of WWTP from biogas | 88.06% | % of consumption
▪ Thermal energy
CHP: Thermal energy generation efficiency | 50 | % | (Same assumption as above for CAS + Digestion)
Thermal energy generation | 4825.08 | kWh/d
| 1761154.2 | kWh/year
GREENHOUASE GAS (GHG) EMISSIONS REDUCTION
Local GHG emissions for electricity generation | 565 | g CO2/kWh
Production of electricity from renewable biogas | 1056692.52 | kWh/year
GHG emission reduction through electricity from biogas | -597.0313 | tons CO2e/year | This is the (saved) fossil CO2e emission that is avoided through renewable biogas utilization for power generation.
Elimination of existing GHG emissions from digester | 0 | tons CO2e/year | The biogas in question can only be considered if it was emitted already before this project; if the biogas is generated and utilized by the project, it cannot be considered an emission reduction.
Total GHG emission reduction | -597.0313 | tons CO2e/year
OPEX SAVINGS
Electricity tariff | 0.15 | US$/kWh
Reduction of electricity cost | -434.2572 | US$/d | (Saving equals electricity production from biogas)
| -158503.878 | US$/year
Sludge disposal unit cost | 10 | US$/m3
Reduction of sludge disposal cost | -7.3544 | m³/d
| -2684.3687 | m³/year
| -26843.687 | US$/year
Additional labor hour cost | 10000 | US$/personnel/year
| 15000 | US$/year | (Same assumption as above for CAS + Digestion)
Additional maintenance cost | 37353.3823 | US$/year | (Same assumption as above for CAS + Digestion)
Total OPEX saving | -132994.1827 | US$/year
INSTALLATION REQUIREMENTS
Primary Sedimentation Tank | 1250 | m³
Pre-treatment of organic waste | Check specific requirements! | ---
Digester volume | 1574.5714 | m³
Biogas holder | 296.928 | m³
CHP - total electric power | 144.7524 | kW | Assumption: avg. operation time = 20 h/d
| 72.3762 | kW / unit | Based on 2 units
Biogas cleaning | Check specific requirements! | ---
Biogas pipe system, flare, etc | Check specific requirements! | ---
UASB | Value | Unit | Comment
WASTEWATER TREATMENT
▪ UASB
Average influent BOD5 load | 4800 | kg/d
Average influent TSS load | 4800 | kg/d
SLUDE PRODUCTION
▪ Secondary sludge
Daily raw UASB-S production (DS) | 0.3 | gDS/gBOD5 | Typical: 0.3 (0.2-0.4)
| 1440 | kgDS/d
DS of sludge when removed from UASB | 3.5 | %DS | Typical: 3.5 (3-5)%
DS of UASB-S after thickening | 4 | %DS | Gravity thickener: 3-6%.
VS/DS of UASB-S after thickening | 56 | %VS | Typical: 56% (50-60%)
Daily UASB-S production, thickened (m3) | 36 | m³/d
SLUDGE FOR DISPOSAL / REUSE
DS after sludge dewatering | 24 | %DS | Typical: 24 (20-35)
Total average DS production | 1440 | kgDS/d
Total specific DS production | 18 | gDS/PE60/d
| 15 | gDS/cap/d
Total average dewatered sludge production | 6 | m³/d
| 2190 | m³/year
BIO GAS PRODUCTION
Biogas holder volume | 20 | % of daily gas production | (Same assumption as above for CAS + Digestion)
Required biogas holder volume | 208.32 | m³
▪ Biogas yield
Biogas yield from influent pollution load | 217 | L/kgBOD5,added/d | Typical: 217 (115-280)
▪ Biogas production
Biogas production | 1041.6 | m³/d
| 380184 | m³/year
Total specific biogas production | 13.02 | L/PE60/d | Typical: 13 (7-16)
| 10.85 | L/cap/d
▪ Methane content of biogas
Methane in biogas from UASB | 65 | % CH4 | Typical: 65 (60-80)%
ENERGY FROM BIOGAS
Calorific value of biogas | 6.5 | kWh/m3
▪ Electricity
CHP: Electric energy generation efficiency | 30 | % | Typical: co-generation: 30-40%, microturbine: 28-33%, or see figure above for CAS + Digestion
Electricity generation from biogas | 2031.12 | kWh/d
| 9.267 | kWh/PE60/year
| 741358.8 | kWh/year
Electricity consumption of UASB-WWTP | 8 | kWh/PE60/year | Typical: 8 (2-13)
| 1777.7778 | kWh/d
| 648888.8889 | kWh/year
Electricity coverage of WWTP from biogas | 114.3% | % of consumption
▪ Thermal energy
CHP: Thermal energy generation efficiency | 50 | % | Typical: 50 (50-55)%
Thermal energy generation | 3385.2 | kWh/d
| 1235598 | kWh/year
GREENHOUASE GAS (GHG) EMISSIONS REDUCTION
Local GHG emissions for electricity generation | 565 | g CO2/kWh
Production of electricity from renewable biogas | 741358.8 | kWh/year
GHG emission reduction through electricity from biogas | -418.8677 | tons CO2e/year | This is the (saved) fossil CO2e emission that is avoided through renewable biogas utilization for power generation.
Biogas emission prior to this WWTP project | 0 | m³/year
Methane emission prior to this WWTP project | 0 | m³/year
GHG factor of methane | 21 | --- | This factor indicates how much stronger a GHG is methane than CO2
Specific weight of methane | 0.72 | kg/m3 methane
Elimination of existing GHG emissions from UASB | 0 | tons CO2e/year | The biogas in question can only be considered if it was emitted already before this project; if the biogas is generated and utilized by the project, it cannot be considered an emission reduction.
Total GHG emission reduction | -418.8677 | tons CO2e/year
OPEX SAVINGS
Electricity tariff | 0.15 | US$/kWh
Reduction of electricity cost | -304.668 | US$/d | (Saving equals electricity production from biogas)
| -111203.82 | US$/year
Additional O&M cost for CHP | 17413.2287 | US$/year | (The value, which is calculated here is based upon additional maintenance cost for CHP per kWh produced = 12.321 x kWelectr(-0.422)). Dependant on size of CHP this implicates OPEX of 0.5-4.0 Cent/kWhelectr
Total OPEX saving | -93790.5913 | US$/year
INSTALLATION REQUIREMENTS
Biogas holder | 208.32 | m³
CHP - total electric power | 101.556 | kW | Assumption: avg. operation time = 20 h/d
| 50.778 | kW / unit | Based on 2 units
Biogas cleaning | Check specific requirements! | ---
COVERED ANAEROBIC POND | Value | Unit | Comment
WASTEWATER TREATMENT
▪ Covered Anaerobic Pond
Average influent BOD5 load | 4800 | kg/d
Average influent TSS load | 4800 | kg/d
SLUDE PRODUCTION
▪ Secondary sludge
Daily raw AP-S production (DS) | 6 | kgDS/cap/y | Typical: 6 (4-10)
| 1578.0822 | kgDS/d
DS of sludge when removed from AP | 6 | %DS | Typical: 6 (5-10)%
VS/DS of AP-S | 55 | %VS | Typical: 55 (50-60)%
Daily AP-S production, thickened (m3) | 26.3014 | m³/d
SLUDGE FOR DISPOSAL / REUSE
DS after sludge dewatering | 25 | %DS | Typical: 25 (20-35)
Total average DS production | 1578.0822 | kgDS/d
Total specific DS production | 19.726 | gDS/PE60/d
| 16.4384 | gDS/cap/d
Total average dewatered sludge production | 6.3123 | m³/d
| 2304 | m³/year
BIO GAS PRODUCTION
▪ Biogas yield
Methane yield from influent pollution load | 180 | L CH4/kgBOD5 | Typical: 180 (160-230)
Biogas yield from influent pollution load | 257.1429 | L/kgBOD5,added/d | Typical: 250 (230-330)
▪ Biogas production
CH4 production | 864 | m³/d
Biogas production | 1234.2857 | m³/d
| 450514.2857 | m³/year
Total specific biogas production | 15.4286 | L/PE60/d | Typical: 14-20
| 12.8571 | L/cap/d
▪ Methane content of biogas
Methane in biogas from AP | 70 | % CH4 | Typical: 70 (60-80)%
ENERGY FROM BIOGAS
Calorific value of biogas | 7 | kWh/m3
▪ Electricity
CHP: Electric energy generation efficiency | 30 | % | Typical: co-generation: 30-40%, microturbine: 28-33%, or see figure above for CAS + Digestion
Electricity generation from biogas | 2592 | kWh/d
| 11.826 | kWh/PE60/year
| 946080 | kWh/year
Electricity consumption of AP-WWTP | 3 | kWh/PE60/year | Typical: 1-3, mainly dependant on pumping requirements (see figure)
| 666.6667 | kWh/d
| 243333.3333 | kWh/year
Electricity coverage of WWTP from biogas | 388.8% | % of consumption
▪ Thermal energy
CHP: Thermal energy generation efficiency | 50 | % | Typical: 50 (50-55)%
Thermal energy generation | 4320 | kWh/d
| 1576800 | kWh/year
GREENHOUASE GAS (GHG) EMISSIONS REDUCTION
Local GHG emissions for electricity generation | 565 | g CO2/kWh
Production of electricity from renewable biogas | 946080 | kWh/year
GHG emission reduction through electricity from biogas | -534.5352 | tons CO2e/year | This is the (saved) fossil CO2e emission that is avoided through renewable biogas utilization for power generation.
Biogas emission prior to this WWTP project | 0 | m³/year
Methane emission prior to this WWTP project | 0 | m³/year
GHG factor of methane | 21 | --- | This factor indicates how much stronger a GHG is methane than CO2
Specific weight of methane | 0.72 | kg/m3 methane
Elimination of existing GHG emissions from Anaerobic Ponds | 0 | tons CO2e/year | The biogas in question can only be considered if it was emitted already before this project; if the biogas is generated and utilized by the project, it cannot be considered an emission reduction.
Total GHG emission reduction | -534.5352 | tons CO2e/year
OPEX SAVINGS
Electricity tariff | 0.15 | US$/kWh
Reduction of electricity cost | -388.8 | US$/d | (Saving equals electricity production from biogas)
| -141912 | US$/year
Additional O&M cost for CHP | 20048.8362 | US$/year | (The value, which is calculated here is based upon additional maintenance cost for CHP per kWh produced = 12.321 x kWelectr(-0.422)). Dependant on size of CHP this implicates OPEX of 0.5-4.0 Cent/kWhelectr
Additional O&M cost for covers | 4800 | US$/year | (The value, which is calculated here is based upon the following assumptions: (i) cover area is derived from retention time in AP = 2d, water depth = 5m, (ii) unit cover cost = 15 US$/m2, (iii) O&M cost = 2% of CAPEX)
Total OPEX saving | -117063.1638 | US$/year
INSTALLATION REQUIREMENTS
Cover on AP | Check specific design of APs! | m2
CHP - total electric power | 129.6 | kW | Assumption: avg. operation time = 20 h/d
| 64.8 | kW / unit | Based on 2 units
Biogas cleaning | Check specific requirements! | ---
Biogas pipe system, flare, etc | Check specific requirements! | ---
De-locking key: W2E